## First Iteration
Alert | Measure | Time | Date | Condition | Note | Table Name | Value in table
1 | Water | 00:00-06:00 | Any | >10 |  | N/A
2 | Irrigation | any | Nov- Apr | >1000 |  | N/A
3 | Lighting | 00:00-06:00 | any | >1 |  | CEVAC_x_POWER_LATEST | Building Lighting actualvalue
4 | Temperature | any | any | +/- 2 SP | Supress 30 min at SP change times | CEVAC_x_TEMP_LATEST | All rooms
5 | Chilled Water | any | Nov- Apr | >500,000 |  | N/A
6 | Steam | any | Apr-Nov | >200,000 |  | N/A
7 | Total Electrical Usage | any | Sat-Sun | >300 |  | CEVAC_x_POWER_LATEST | sum of all actualvalue
8 | Total Electrical Usage | 00:00-06:00 | any | >300 |  | CEVAC_x_POWER_LATEST | sum of all actualvalue
9 | Total Electrical Usage | any | Any | >550 |  | CEVAC_x_POWER_LATEST | sum of all actualvalue
12 | Emergency | any | any | >80 |  | CEVAC_x_POWER_LATEST | sum of 3rd floor emergency and basement emergency
14 | CO2 |  |  | 1000 warn, 2000 alarm |  | CEVAC_x_IAQ_LATEST | all sensors
10 | Any | any | any | null/empty |  | all

## Second Iteration
alert_name | type | alias | units | message | building | database | column | sort_column | num_entries | time_dependent | hour | day | month | occupied | condition | value | operation
Watt_CO2_warning | CO2 | * | ppm | <alias> exceeds 1000 ppm | WATT | CEVAC_WATT_IAQ_LATEST | ActualValue | UTCDateTime | 1 | 1 | 8-23 | * | * | 1 | > | 1000 | warning
Watt_CO2_alert | CO2 | * | ppm | <alias> exceeds 2000 ppm | WATT | CEVAC_WATT_IAQ_LATEST | ActualValue | UTCDateTime | 1 | 0 | * | * | * | * | > | 2000 | alert
Watt_Media_lights_summer_warning | Power | Building Media Lights | kW | The Media lights are on. | WATT | CEVAC_WATT_POWER_LATEST | ActualValue | UTCDateTime | 1 | 1 | 0-8 & 17-23 | * | 5-8 | 0 | > | 1 | warning
Watt_Media_lights_schoolyear_warning | Power | Building Media Lights | kW | The Media lights are on. | WATT | CEVAC_WATT_POWER_LATEST | ActualValue | UTCDateTime | 1 | 1 | 0-6 & 20-23 | * | 1-4 & 9-12 | 0 | > | 1 | warning
Watt_1F_Light_summer_warning | Power | 1st Floor Lighting | kW | 1st Floor Lights are on. | WATT | CEVAC_WATT_POWER_LATEST | ActualValue | UTCDateTime | 1 | 1 | 0-8 & 17-23 | 1-5 | 5-8 | 0 | > | 1.3 | warning
Watt_1F_Light_schoolyear_warning | Power | 1st Floor Lighting | kW | 1st Floor Lights are on. | WATT | CEVAC_WATT_POWER_LATEST | ActualValue | UTCDateTime | 1 | 1 | 0-6 & 20-23 | 1-5 | 1-4 & 9-12 | 0 | > | 1.3 | warning
Watt_1F_Light_weekend_warning | Power | 1st Floor Lighting | kW | 1st Floor Lights are on. | WATT | CEVAC_WATT_POWER_LATEST | ActualValue | UTCDateTime | 1 | 1 | * | 6-7 | * | 0 | > | 1.3 | warning
Watt_2F_Light_summer_warning | Power | 2nd Floor Lighting | kW | 2nd Floor Lights are on. | WATT | CEVAC_WATT_POWER_LATEST | ActualValue | UTCDateTime | 1 | 1 | 0-8 & 17-23 | 1-5 | 5-8 | 0 | > | 1.15 | warning
Watt_2F_Light_schoolyear_warning | Power | 2nd Floor Lighting | kW | 2nd Floor Lights are on. | WATT | CEVAC_WATT_POWER_LATEST | ActualValue | UTCDateTime | 1 | 1 | 0-6 & 20-23 | 1-5 | 1-4 & 9-12 | 0 | > | 1.15 | warning
Watt_2F_Light_weekend_warning | Power | 2nd Floor Lighting | kW | 2nd Floor Lights are on. | WATT | CEVAC_WATT_POWER_LATEST | ActualValue | UTCDateTime | 1 | 1 | * | 6-7 | * | 0 | > | 1.15 | warning
Watt_3F_Light_summer_warning | Power | 3rd Floor Lighting | kW | 3rd Floor Lights are on. | WATT | CEVAC_WATT_POWER_LATEST | ActualValue | UTCDateTime | 1 | 1 | 0-8 & 17-23 | 1-5 | 5-8 | 0 | > | 1.35 | warning
Watt_3F_Light_schoolyear_warning | Power | 3rd Floor Lighting | kW | 3rd Floor Lights are on. | WATT | CEVAC_WATT_POWER_LATEST | ActualValue | UTCDateTime | 1 | 1 | 0-6 & 20-23 | 1-5 | 1-4 & 9-12 | 0 | > | 1.35 | warning
Watt_3F_Light_weekend_warning | Power | 3rd Floor Lighting | kW | 3rd Floor Lights are on. | WATT | CEVAC_WATT_POWER_LATEST | ActualValue | UTCDateTime | 1 | 1 | * | 6-7 | * | 0 | > | 1.35 | warning
Watt_4F_Light_summer_warning | Power | 4th Floor Lighting | kW | 4th Floor Lights are on. | WATT | CEVAC_WATT_POWER_LATEST | ActualValue | UTCDateTime | 1 | 1 | 0-8 & 17-23 | 1-5 | 5-8 | 0 | > | 1 | warning
Watt_4F_Light_schoolyear_warning | Power | 4th Floor Lighting | kW | 4th Floor Lights are on. | WATT | CEVAC_WATT_POWER_LATEST | ActualValue | UTCDateTime | 1 | 1 | 0-6 & 20-23 | 1-5 | 1-4 & 9-12 | 0 | > | 1 | warning
Watt_4F_Light_weekend_warning | Power | 4th Floor Lighting | kW | 4th Floor Lights are on. | WATT | CEVAC_WATT_POWER_LATEST | ActualValue | UTCDateTime | 1 | 1 | * | 6-7 | * | 0 | > | 1 | warning
Watt_BSMT_Light_summer_warning | Power | Basement Lighting | kW | Basement Lights are on. | WATT | CEVAC_WATT_POWER_LATEST | ActualValue | UTCDateTime | 1 | 1 | 0-8 & 17-23 | 1-5 | 5-8 | 0 | > | 1 | warning
Watt_BSMT_Light_schoolyear_warning | Power | Basement Lighting | kW | Basement Lights are on. | WATT | CEVAC_WATT_POWER_LATEST | ActualValue | UTCDateTime | 1 | 1 | 0-6 & 20-23 | 1-5 | 1-4 & 9-12 | 0 | > | 1 | warning
Watt_4F_Light_schoolyear_warning | Power | Basement Lighting | kW | Basement Lights are on. | WATT | CEVAC_WATT_POWER_LATEST | ActualValue | UTCDateTime | 1 | 1 | * | 6-7 | * | 0 | > | 1 | warning
Watt_Emergency_Power_alert | Power | Building Emergency | kW | Building emergency power > 80 kW | WATT | CEVAC_WATT_POWER_LATEST | ActualValue | UTCDateTime | 1 | 0 | * | * | * | * | > | 80 | alert
Watt_Power_night_summer_warning | Power | * | kW | Building power usage > 300 kW | WATT | CEVAC_WATT_POWER_SUMS_LATEST | ActualValue | UTCDateTime | 1 | 1 | 0-8 & 17-23 | 1-5 | 5-8 | 0 | > | 300 | warning
Watt_Power_weekend_warning | Power | * | kW | Building power usage > 300 kW | WATT | CEVAC_WATT_POWER_SUMS_LATEST | ActualValue | UTCDateTime | 1 | 1 | * | 6-7 | * | 0 | > | 300 | warning
Watt_Power_night_schoolyear_warning | Power | * | kW | Building power usage > 300 kW | WATT | CEVAC_WATT_POWER_SUMS_LATEST | ActualValue | UTCDateTime | 1 | 1 | 0-6 & 20-23 | 1-5 | 1-4 & 9-12 | 0 | > | 300 | warning
Watt_Temperature_high_warning | Temperature | * | degF | <alias> is above its Cooling SP | WATT | CEVAC_WATT_TEMP_DAY | ActualValue | UTCDateTime | 2 | 0 | * | * | * | * | > | <alias- " Temp"> Cooling SP | warning
Watt_Temperature_high_alert | Temperature | * | degF | <alias> is above its Cooling SP by 3 degrees or more | WATT | CEVAC_WATT_TEMP_DAY | ActualValue | UTCDateTime | 2 | 0 | * | * | * | * | > | <alias- " Temp"> Cooling SP+3 | alert
Watt_Temperature_low_warning | Temperature | * | degF | <alias> is below its Heating SP | WATT | CEVAC_WATT_TEMP_DAY | ActualValue | UTCDateTime | 2 | 0 | * | * | * | * | < | <alias- " Temp"> Heating SP | warning
Watt_Temperature_low_alert | Temperature | * | degF | <alias> is below its Heating SP by 3 degrees or more | WATT | CEVAC_WATT_TEMP_DAY | ActualValue | UTCDateTime | 2 | 0 | * | * | * | * | < | <alias- " Temp"> Heating SP-3 | alert
Watt_CO2_null_alert | CO2 | * | ppm | <alias> has not reported in more than an hour | WATT | CEVAC_WATT_IAQ_LATEST_FULL | UTCDateTime | UTCDateTime | 1 | 0 | * | * | * | * | < | <now> - 1 day | alert
Watt_Power_Null_alert | Power | * | kW | <alias> has not reported in more than an hour | WATT | CEVAC_WATT_POWER_LATEST | UTCDateTime | UTCDateTime | 1 | 0 | * | * | * | * | < | <now> - 1 hr | alert
Watt_Temperature_Null_alert | Temperature | * | degF | <alias> has not reported in more than an hour | WATT | CEVAC_WATT_TEMP_LATEST | UTCDateTime | UTCDateTime | 1 | 0 | * | * | * | * | < | <now> - 1 hr | alert

## Third Iteration
alert_name | type | alias | units | alert_message | bldg_std | bldg_disp | database | column | sort_column | num_entries | time_dependent | occupancy_status | condition | value | alert_type | message_ID
Watt_CO2_warning | CO2 | * | ppm | <alias> exceeds 1000 ppm. | WATT | Watt | CEVAC_WATT_IAQ_LATEST | ActualValue | UTCDateTime | 1 | 1 | 1 | > | 1000 | warning | 1
Watt_CO2_alert | CO2 | * | ppm | <alias> exceeds 2000 ppm. | WATT | Watt | CEVAC_WATT_IAQ_LATEST | ActualValue | UTCDateTime | 1 | 0 | * | > | 2000 | alert | 2
1st_Floor_Lights | Power | 1st Floor Lighting | kW | 1st Floor Lights are on. | WATT | Watt | CEVAC_WATT_POWER_LATEST | ActualValue | UTCDateTime | 1 | 1 | 0 | > | 1.3 | alert | 3
2nd_Floor_Lights | Power | 2nd Floor Lighting | kW | 2nd Floor Lights are on. | WATT | Watt | CEVAC_WATT_POWER_LATEST | ActualValue | UTCDateTime | 1 | 1 | 0 | > | 1.15 | alert | 4
3rd_Floor_Lights | Power | 3rd Floor Lighting | kW | 3rd Floor Lights are on. | WATT | Watt | CEVAC_WATT_POWER_LATEST | ActualValue | UTCDateTime | 1 | 1 | 0 | > | 1.35 | alert | 5
4th_Floor_Lights | Power | 4th Floor Lighting | kW | 4th Floor Lights are on. | WATT | Watt | CEVAC_WATT_POWER_LATEST | ActualValue | UTCDateTime | 1 | 1 | 0 | > | 1 | alert | 6
Media_Lights | Power | Building Media Lights | kW | The Media Lights are on. | WATT | Watt | CEVAC_WATT_POWER_LATEST | ActualValue | UTCDateTime | 1 | 1 | 0 | > | 1 | alert | 7
Temp_High_warning | Temperature | * | deg-F | <alias> reads <ActualValue> [deg-F] (Cooling SP = <Cooling SP> [deg-F]) | WATT | Watt | CEVAC_WATT_TEMP_DAY | ActualValue | UTCDateTime | 3 | 0 | * | > | <Cooling SP ActualValue> | warning | 8
Temp_High_alert | Temperature | * | deg-F | <alias> reads <ActualValue> [deg-F] (Cooling SP = <Cooling SP> [deg-F]) | WATT | Watt | CEVAC_WATT_TEMP_LATEST | ActualValue | UTCDateTime | 1 | 0 | * | > | <Cooling SP ActualValue>+3 | alert | 9
Temp_Low_warning | Temperature | * | deg-F | <alias> reads <ActualValue> [deg-F] (Heating SP = <Heating SP> [deg-F]) | WATT | Watt | CEVAC_WATT_TEMP_DAY | ActualValue | UTCDateTime | 3 | 0 | * | < | <Heating SP ActualValue> | warning | 10
Temp_Low_alert | Temperature | * | deg-F | <alias> reads <ActualValue> [deg-F] (Heating SP = <Heating SP> [deg-F]) | WATT | Watt | CEVAC_WATT_TEMP_LATEST | ActualValue | UTCDateTime | 1 | 0 | * | < | <Heating SP ActualValue> -3 | alert | 11
Building_Emergency_Power_alert | Power | Building Emergency | kW | Building emergency power exceeds 80 kW. | WATT | Watt | CEVAC_WATT_POWER_LATEST | ActualValue | UTCDateTime | 1 | 0 | * | > | 80 | alert | 12
Building_Power_Unoccupied_alert | Power | * | kW | The building is unoccupied but is using a lot of power. | WATT | Watt | CEVAC_WATT_POWER_SUMS_LATEST | ActualValue | UTCDateTime | 1 | 1 | 0 | > | 300 | alert | 13
Dead_Temp_sensor_alert | Temperature | * | deg-F | <alias> has not reported recently. | WATT | Watt | CEVAC_WATT_TEMP_LATEST | UTCDateTime | UTCDateTime | 1 | 0 | * | < | <now> - 1 hr | alert | 14
Dead_Power_sensor_alert | Power | * | kW | <alias> has not reported recently. | WATT | Watt | CEVAC_WATT_POWER_LATEST | UTCDateTime | UTCDateTime | 1 | 0 | * | < | <now> - 1 hr | alert | 15
Dead_IAQ_sensor_alert | CO2 | * | ppm | <alias> has not reported recently. | WATT | Watt | CEVAC_WATT_IAQ_LATEST | UTCDateTime | UTCDateTime | 1 | 0 | * | < | <now> - 1 hr | alert | 16